YT industrial Large RO systems 250-42000gpd

| RS - 250 ~ RS - 800 | SA -1500 ~ SA - 9000 |
| --- | --- |

| LA - 5000 ~ LA - 10000 | LA2 - 12000 ~ LA2 - 18000 |
| --- | --- |
| LBW - 35 ~ LBW - 70 | For larger capacity R.O System, please contact us.. Custom-made design is available upon request.. Additional options:. Ultra - Filtration System, K-PLUS Series Deionizer And Mixed-Bed Deionizer.. |
| Operation Pressure : 150 -220 PSI Rejection : >97% (Organic, colloids, bacteria, and pyrogen are above 99.9% rejected.) Recovery Rate: 50% ~ 75% |  |

RO ALL SPECIFICATIONS

| Model# | Flow Rates (GPD) |  | R.O Modules (Model x Numers) |  | R.O Pump / Voltage |  | Pre - Filter | Dimensions (cm) & Weight (kg) |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| RS - 250 RS - 500 SR - 800 | 250 500 800 |  | 2521*1 2521*2 4021*1 |  | 1/3HP,110V/220V 1/3HP,110V/220V 1/2HP,110V/220V |  | 5m, 20" * 1 1m, 20" * 1 | 73*40*113*56 73*40*113*58 73*40*113*60 |  |
| SA - 1500 SA - 3000 SA - 4500 SA - 6000 SA - 7500 SA - 9000 | 1500 3000 4500 6000 7500 9000 |  | 4040*1 4040*2 4040*3 4040*4 4040*5 4040*6 |  | 1HP,110V/220V 3HP,220V/380V 3HP,220V/380V 4HP,220V/380V 5.5HP,220V/380V 5.5HP,220V/380V |  | 5m, 20" * 1 5m, 20" * 1 5m, 20" * 1 5m, 20" * 2 5m, 20" * 2 5m, 20" * 2 | 90*70*154*83 90*70*154*150 90*70*154*168 90*70*154*188 90*70*154*210 90*70*154*232 |  |
| SA - 5000 SA - 7500 LA - 10000 | 5000 7500 10000 |  | 4060*2 4060*3 4060*4 |  | 3HP,220V/380V 5.5HP,220V/380V 5.5HP,220V/380V |  | TK10 * 1 TK10 * 1 TK10 * 1 | 210*70*178 |  |
| LA2 - 12000 LA2 - 15000 LA2 - 18000 | 12000 15000 18000 |  | 4080*4 4080*5 4080*6 |  | 5.5HP,220V/380V 5.5HP,220V/380V 5.5HP,220V/380V |  | TK10 * 1 TK10 * 1 TK10 * 1 | 210*70*178 |  |
| LBW - 35 LBW - 50 LBW - 70 | 21000 30000 42000 |  | 4080*2 4080*3 4080*4 |  | 5.5HP,220V/380V 7.5HP,220V/380V 15HP,220V/380V |  | TK14 * 1 TK21 * 1 TK21 * 1 | 230*80*178 |  |
| Notes: |  |  |  |  |  |  |  |  |  |
| Feedwater Conditions |  |  |  |  |  |  |  |  |  |
| Inlet Pressure ------------- |  | > 1.5 kg/cm2 |  | Chlorine -------------- |  | < 0.1 ppm |  |  |  |
| Total Hardness ----------- |  | <10 ppm |  | Turbidity ------------- |  | < 2 NTU |  |  |  |
| Fe ----------------------------- |  | < 0.1 ppm |  | SDI -------------------- |  | < 4 |  |  |  |

| Features |  |  |
| --- | --- | --- |
| a.; Automatically operates and PLC control device.. b.; Automatic flush device.. c.; Low-pressure protection switch.. d.; Product Hi-level control.. e.; Over - heat protection device for pump.. f.; Concentrate recycle-flow regulator.. g.; Digital feed/ product water quality meter.. | h.; Operating pressure set-up device.. i.; Automatic power shut-off device if pre-treatment system is in regeneration process.. j.; Chemical cleaning system.. k.; All # SUS 304 made skids except the RS-series.. l.; Includes one standard Hi-pressure R.O Pump; optional two parallel Hi-pressure R.O Pumps are also available.. |

DM-W-RO ALL -250-42000-單主機規格表-200508